Copyright 2019 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 260519 - LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

See "Sustainable Design Considerations" Article in the Evaluations for a discussion of sustainable design requirements that may impact editing of this Section.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Copper building wire.

          - Aluminum building wire.

          - Nonmetallic Underground conduit with conductors, Type NUCC.

          - Armored cable, Type AC.

          - Photovoltaic cable, Type PV.

          - Mineral-insulated cable, Type MI.

          - Tray cable, Type TC.

          - Fire-alarm wire and cable.

          - Connectors and splices.

        - Related Requirements:

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 260513 "Medium-Voltage Cables" for single-conductor and multiconductor cables, cable splices, and terminations for electrical distribution systems with 601 to 35,000 V.

          - Section 260523 "Control-Voltage Electrical Power Cables" for control systems communications cables and Classes 1, 2, and 3 control cables.

          - Section 271313 "Communications Copper Backbone Cabling" for twisted pair cabling used for data circuits.

          - Section 271513 "Communications Copper Horizontal Cabling" for twisted pair cabling used for data circuits.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

        - Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED v4 for Healthcare, MR Credit, "PBT Source Reduction - Lead, Cadmium, and Copper."

          - Product Data: For each conductor and cable indicating lead content.

Retain "Product Data" Subparagraph below to require minimum recycled content for LEED 2009, MRc 2 "Recycled Content."

          - Product Data: For recycled content, indicating postconsumer and preconsumer recycled content and cost.

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; and Green Globes. Coordinate with requirements.

          - Product Data: For solvents and adhesives, indicating VOC content.

"Laboratory Test Reports" Subparagraph below is an additional requirement for schools projects.

          - Laboratory Test Reports: For solvents and adhesives, indicating compliance with requirements for low-emitting materials.

        - Product Schedule: Indicate type, use, location, and termination locations.

      - INFORMATIONAL SUBMITTALS

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - QUALITY ASSURANCE

        - Regulatory Requirements:

          - Conform to requirements of ANSI/NFPA 70/CSA.

          - Conform to requirements of Electrical Circuit Protective System listing in UL/ULC Fire Resistance Directory.

          - Provide products listed by UL/ULC as suitable for the purpose specified.

      - DELIVERY, STORAGE, AND HANDLING

This article is based on nVent PYROTENAX fire-rated cable requirements. Retain as applicable.

        - Cables shall be shipped from manufacturer with ends sealed against moisture.

        - Storage:

          - Protect exposed cable ends with shrinkable, molded polyolefin end caps or other suitable means such as hot-melt glue and/or heat-shrink tubing.

          - Store cable in clean, dry location.

        - Handling:

          - Uncoil cable by rolling or rotating supply reel.

          - Take precautions necessary to prevent damage to cable from contact with sharp objects, such as when pulled over foreign material on sheaves.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

For more detailed information on PYROTENAX's Product Warranty, see www.nvent.com/PYROTENAX

.

As a demonstration of quality, PYROTENAX, a brand of nVent offers a 30-year warranty on all cable and components manufactured. Contractor (or PYROTENAX's field technician) must perform a system test as outlined in PYROTENAX's installation manual. The warranty being offered is required to be published on manufacturer's website.

        - Manufacturer's Warranty: Provide Owner a product warranty for fire-rated wiring products described below.

          - Contractor must complete insulation resistance testing prior to Commissioning and maintain records of test results.

          - Warranty Period for Wiring Cable: Lifetime.

          - Warranty information must be published on manufacturer's website.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - COPPER BUILDING WIRE

Retain this article to specify allowable types of copper building wire. Separate articles are included in the Specification for aluminum building wire, Type AC cable (copper and aluminum), and Type PV cable.

        - Description: Flexible, insulated and uninsulated, drawn copper current-carrying conductor with an overall insulation layer or jacket, or both, rated 600 V or less.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - Alpha Wire Company.

          - American Bare Conductor.

          - Belden Inc.

          - Encore Wire Corporation.

          - Okonite Company (The).

          - Service Wire Co.

          - Southwire Company.

          - <Insert manufacturer's name>.

        - Standards:

          - Listed and labeled as defined in NFPA 70/CSA 22 part 2, by a qualified testing agency, and marked for intended location and use.

See the Evaluations for discussion of UL's "Wire and Cable Marking and Application Guide."

          - Conductor and Cable Marking: Comply with wire and cable marking in accordance with UL's "Wire and Cable Marking and Application Guide."

First option in "Conductors" Paragraph below is standard for most conductors. Second option is specific to Type TC-ER cables or larger conductors requiring compact stranding.

        - Conductors: Copper, complying with ASTM B3 for bare annealed copper and with [ASTM B8] [ASTM B496] for stranded conductors.

Common insulation types are described below; however, numerous other insulation types and flame-resistance options are available. Coordinate with Drawings.

        - Conductor Insulation:

          - Type NM: Comply with UL 83 and UL 719.

          - Type RHH: Comply with UL 44.

          - [Type USE-2] [and] [Type SE]: Comply with UL 854.

          - [Type THHN] [and] [Type THWN-2]: Comply with UL 83.

          - [Type THW] [and] [Type THW-2]: Comply with NEMA WC-70/ICEA S-95-658 and UL 83.

          - Type UF: Comply with UL 83 and UL 493.

          - Type XHHW-2: Comply with UL 44.

          - <Insert Type and standard>.

      - ALUMINUM BUILDING WIRE

Retain this article to specify allowable types of aluminum building wire. Separate articles are included in the Specification for copper building wire, Type AC cable (copper and aluminum), Type MC cable (copper and aluminum), and Type PV cable. If retaining multiple types of conductor or cable, indicate where used on Drawings.

        - Description: Flexible, insulated and uninsulated, drawn aluminum current-carrying conductor with an overall insulation layer or jacket, or both, rated 600 V or less.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - Alpha Wire Company.

          - American Bare Conductor.

          - Belden Inc.

          - Encore Wire Corporation.

          - Okonite Company (The).

          - Southwire Company.

          - <Insert manufacturer's name>.

        - Standards:

          - Listed and labeled as defined in NFPA 70/CSA 22 part 2, by a qualified testing agency, and marked for intended location and use.

See the Evaluations for discussion of UL's "Wire and Cable Marking and Application Guide."

          - Conductor and Cable Marking: Comply with wire and cable marking in accordance with UL's "Wire and Cable Marking and Application Guide."

        - Conductors: Aluminum, complying with ASTM B800 and ASTM B801.

Common insulation types are described below; however, numerous other insulation types and flame-resistance options are available. Coordinate with Drawings.

        - Conductor Insulation:

          - Type NM: Comply with UL 83 and UL 719.

          - Type RHH: Comply with UL 44.

          - [Type USE-2] [and] [Type SE]: Comply with UL 854.

          - [Type THHN] [and] [Type THWN-2]: Comply with UL 83.

          - [Type THW] [and] [Type THW-2]: Comply with NEMA WC-70/ICEA S-95-658 and UL 83.

          - Type XHHW-2: Comply with UL 44.

          - <Insert Type and standard>.

      - NONMETALLIC UNDERGROUND CONDUIT WITH CONDUCTORS, TYPE NUCC

        - Description: A factory assembly of conductors or cables inside a nonmetallic, smooth wall raceway with a circular cross section.

        - Applicable Standards:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70 and marked for intended location and use.

          - General Characteristics:

            - Reference Standards: UL 1990.

      - ARMORED CABLE, TYPE AC

If retaining multiple types of conductor or cable, indicate where used on Drawings.

        - Description: A factory assembly of insulated current-carrying conductors with or without an equipment grounding conductor in an overall metallic sheath.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - AFC Cable Systems; a part of Atkore International.

          - Alpha Wire Company.

          - American Bare Conductor.

          - Belden Inc.

          - Encore Wire Corporation.

          - Okonite Company (The).

          - Service Wire Co.

          - Southwire Company.

          - <Insert manufacturer's name>.

        - Standards:

          - Listed and labeled as defined in NFPA 70/CSA 22 part 2, by a qualified testing agency, and marked for intended location and use.

          - Comply with UL 4.

See the Evaluations for discussion of UL's "Wire and Cable Marking and Application Guide."

          - Conductor and Cable Marking: Comply with wire and cable marking in accordance with UL's "Wire and Cable Marking and Application Guide."

        - Circuits:

Retain first option in first subparagraph below for single-circuit Type AC cable. Retain second option to allow multiple circuits per cable. If retaining both options, indicate where used on Drawings.

          - [Single circuit] [and] [multicircuit with color-coded conductors].

          - Power-Limited Fire-Alarm Circuits: Comply with UL 1424.

        - Conductors: [Copper, complying with ASTM B3 for bare annealed copper and with ASTM B8 for stranded conductors] [Aluminum, complying with ASTM B800 and ASTM B801].

        - Ground Conductor: [Bare] [Insulated] [None].

        - Conductor Insulation: Type THHN/THWN-2. Comply with UL 83.

        - Armor: [Steel] [Aluminum], interlocked.

      - PHOTOVOLTAIC CABLE, TYPE PV

        - Description: Flexible, insulated and uninsulated, drawn copper current-carrying conductor with an overall insulation layer or jacket, or both, rated [2000] [600] V.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - Encore Wire Corporation.

          - Service Wire Co.

          - Southwire Company.

          - <Insert manufacturer's name>.

        - Standards:

          - Listed and labeled as defined in NFPA 70/CSA 22 part 2, by a qualified testing agency, and marked for intended location and use.

See the Evaluations for discussion of UL's "Wire and Cable Marking and Application Guide."

          - Conductor and Cable Marking: Comply with wire and cable marking in accordance with UL's "Wire and Cable Marking and Application Guide."

        - Conductors: Copper, complying with ASTM B3 for bare annealed copper and with ASTM B8 for stranded conductors.

        - Conductor Insulation: Comply with UL 44 and UL 4703.

      - MINERAL-INSULATED CABLE, TYPE MI

Retain this article to specify a Type MI cable for power with a 2-hour fire rating. See the Evaluations for a discussion of Type MI cable and for information on manufacturers who offer Type MI cable.

MI cable is preferred for all applications. The inorganic composition of MI cable does not create additional smoke or contribute to fire. Additionally, when specifying MI cable, neither conduit nor splice/pull boxes are required, and there are no vertical length limits.

        - Description: Solid copper conductors encased in compressed mineral oxide with an outer metallic sheath, rated 600 V or less.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide PYROTENAX, a brand of nVent; System 1850 MI cables or comparable product by one of the following:

          - Watlow Electric Manufacturing Company.

          - <Insert manufacturer's name>.

        - Standards:

          - Listed and labeled as defined in NFPA 70/CSA 22 part 2, by a qualified testing agency, and marked for intended location and use.

          - UL 2196/ULC S139 for fire resistance.

See the Evaluations for discussion of UL's "Wire and Cable Marking and Application Guide."

          - Conductor and Cable Marking: Comply with wire and cable marking in accordance with UL's "Wire and Cable Marking and Application Guide."

        - Properties:

          - Inorganic composition. Polymeric insulation not allowed.  Cables that generate toxic or combustible gases when heated shall not be permitted.

          - Insulation Voltage Rating: 600 volts.

          - Continuous Cable Temperature Rating: 482 deg F (250 deg C).

          - Termination Temperature Rating: 392 deg F (200 deg C).

          - Conduit not required.

        - Conductors: Copper, complying with ASTM B3 for bare annealed copper.

Magnesium oxide insulation is standard for most Type MI power conductors; however, other materials are available. Consult manufacturer.

        - Insulation: Compressed magnesium oxide.

Copper sheaths are standard for most Type MI power conductors; however, other metals may be available. Consult nVent PYROTENAX representative.

        - Sheath: Seamless soft-drawn copper.

        - Optional Jacketing: Low-smoke, zero-halogen polyolefin.

        - Components:

          - Mineral Insulated cable components shall be cCSAus Certified.

          - Splices, Field and Factory:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product.

Refer to nVent PYROTENAX Installation Sheet H59479 for field-installed fire-rated splices. Refer to nVent PYROTENAX Installation Sheet H60102 for non-fire-rated splice.

            - Basis of Design Product: PYROTENAX, a brand of nVent; [FRJ] [FIFRS] [STJ] splices.

          - Terminations, Field and Factory:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product.

Refer to nVent PYROTENAX Installation Sheet H58872 for PyroPak terminations. Refer to nVent PYROTENAX Installation Sheet H58264 or H58290 for QuickTerm Termination System Startup.

            - Basis of Design Product: PYROTENAX, a brand of nVent; [PyroPak] [QuickTerm] [FQT] [PCU] terminations.

      - TRAY CABLE, TYPE TC

If retaining multiple types of conductor or cable, indicate where used on Drawings.

        - Description: A factory assembly of insulated current-carrying conductors with or without an equipment grounding conductor in a nonmetallic jacket.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

          - Alpha Wire Company.

          - Belden Inc.

          - Encore Wire Corporation.

          - Okonite Company (The).

          - Service Wire Co.

          - Southwire Company.

          - <Insert manufacturer's name>.

        - Standards:

          - Listed and labeled as defined in NFPA 70/CSA 22 part 2, by a qualified testing agency, and marked for intended location and use.

          - Comply with UL 1277.

          - Comply with ICEA S-73-532/NEMA WC 57 for Type TC cables used for control, thermocouple extension, and instrumentation.

          - Comply with ICEA S-95-658/NEMA WC 70 for Type TC cables used for power distribution.

See the Evaluations for discussion of UL's "Wire and Cable Marking and Application Guide."

          - Conductor and Cable Marking: Comply with wire and cable marking in accordance with UL's "Wire and Cable Marking and Application Guide."

        - Conductors: [Copper, complying with ASTM B3 for bare annealed copper and with ASTM B8 for stranded conductors] [Aluminum, complying with ASTM B800 and ASTM B801].

        - Ground Conductor: [Bare] [Insulated] [None].

        - Conductor Insulation: Type XHHW-2. Comply with UL 44.

        - Shield: [None] [Metallic].

      - FIRE-ALARM WIRE AND CABLE

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Twisted-pair, shielded, or non-shielded MI cable is preferred for all applications for backbone/multiplex systems, fire alarm, and voice communication. The inorganic composition of MI cable does not create additional smoke or contribute to fire. Additionally, when specifying MI cable, neither conduit nor splice/pull boxes are required, and there are no vertical length limits.

        - Basis-of-Design Product: Subject to compliance with requirements, provide PYROTENAX, a brand of nVent; System 1850 MI cables or comparable product by one of the following:

          - Allied Wire & Cable Inc.

          - CommScope, Inc.

          - Genesis Cable Products; Honeywell International, Inc.

          - Superior Essex Inc.

          - West Penn Wire.

          - <Insert manufacturer's name>.

        - Properties:

          - Inorganic composition. Polymeric insulation is not allowed. Cables that generate toxic or combustible gases when heated shall not be permitted.

          - Insulation Voltage Rating: 300 volts.

          - Cable Temperature Rating: 482 deg F (250 deg C).

          - Termination Temperature Rating: 392 deg F (200 deg C).

          - No conduit required.

        - General Wire and Cable Requirements: NRTL listed and labeled as complying with NFPA 70, Article 760/CSA.

          - Lead Content: Less than 300 parts per million.

NFPA 70 permits wire sizes down to No. 16 AWG.

        - Signaling Line Circuits: Twisted, shielded pair, [not less than] [No. 18 AWG] <Insert wire size> [size as recommended by system manufacturer].

        - Non-Power-Limited Circuits: Solid-copper conductors with 300-V rated, 75 deg C, color-coded insulation, and complying with requirements in UL 2196/ULC-S139 for a two-hour rating.

NFPA 70 permits wire sizes down to No. 18 AWG.

          - Low-Voltage Circuits: No. 16 AWG, minimum, in pathway.

      - CONNECTORS AND SPLICES

        - Description: Factory-fabricated connectors, splices, and lugs of size, ampacity rating, material, type, and class for application and service indicated; listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and use.

Retain "Basis-of-Design Product" Subparagraph below to require a specific product.

        - Basis-of-Design Product: Subject to compliance with requirements, provide PYROTENAX, a brand of nVent; splices and terminations or comparable product by one of the following:

          - ILSCO; Solid copper conductor compatible connectors.

          - Thomas & Betts Corporation; A Member of the ABB Group.

          - <Insert manufacturer's name>.

        - Splices, Field and Factory:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product.

Refer to nVent PYROTENAX Installation Sheet H59479 for field-installed fire-rated splices. Refer to nVent PYROTENAX Installation Sheet H69192 for non-fire-rated splices.

          - Basis of Design Product: PYROTENAX, a brand of nVent; [FRJ] [FIFRS] [STJ] splices.

        - Terminations, Field and Factory:

Retain "Basis-of-Design Product" Subparagraph below to require a specific product.

Refer to nVent PYROTENAX Installation Sheet H58872 for PyroPak terminations. Refer to nVent PYROTENAX Installation Sheet H58264 or H58290 for QuickTerm Termination System Startup.

          - Basis of Design Product: PYROTENAX, a brand of nVent; [PyroPak] [QuickTerm] [FQT] [PCU] terminations.

        - Lugs: One piece, seamless, designed to terminate conductors specified in this Section.

          - Material: [Copper] [Aluminum] [Bronze].

          - Type: [One] [Two] hole with [standard] [long] barrels.

          - Termination: [Compression] [Crimp].

          - Approved for use with solid copper conductors.

- EXECUTION

Refer to nVent PYROTENAX Installation Manual H57864. See www.nvent.com/PYROTENAX for installation videos.

      - CONDUCTOR MATERIAL APPLICATIONS

This article provides examples of material requirements for conductors and cables. Revise to retain requirements for the various types of wire and cable in this Section. Add other applications and materials if required, revise application and materials to suit Project conditions, authorities having jurisdiction, and practice.

        - Feeders:

          - Copper; solid for No. 16 AWG and to 500 kcmil.

        - Branch Circuits:

          - Copper:Solid for No. 16 AWG and to 500 kcmil.

        - Power-Limited Fire Alarm and Control: Solid for No. 8 AWG and smaller.

      - CONDUCTOR INSULATION AND MULTICONDUCTOR CABLE APPLICATIONS AND WIRING METHODS

This article provides examples of application requirements for conductors and cables. Revise to retain wiring methods for various environments in Project. Add other methods if required. Revise conductor insulation and cable type designations to suit Project conditions, authorities having jurisdiction, and practice. See NFPA 70 and UL's "Wire and Cable Marking and Application Guide" for additional application information about conductor sizes, insulation temperature ratings in cables, and product-use classifications and restrictions.

See the Evaluations for use of Type MI cable as service entrance conductor inside a building.

        - Service Entrance: Mineral-insulated, metal-sheathed cable, Type MI.

        - Exposed Feeders: Mineral-insulated, metal-sheathed cable, Type MI.

        - Feeders Concealed in Ceilings, Walls, Partitions, and Crawlspaces: Mineral-insulated, metal-sheathed cable, Type MI.

Coordinate "Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground" Paragraph below with Section 260543 "Underground Ducts and Raceways for Electrical Systems."

Jacketed MI cable required for concrete encasement. Optional for direct burial. Contact nVent PYROTENAX representative for more details.

        - Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground: Jacketed Mineral-insulated, metal-sheathed cable, Type MI.

        - Feeders Installed below Raised Flooring: Mineral-insulated, metal-sheathed cable, Type MI.

        - Feeders in Cable Tray: Mineral-insulated, metal-sheathed cable, Type MI.

        - Exposed Branch Circuits, Including in Crawlspaces: Mineral-insulated, metal-sheathed cable, Type MI.

        - Branch Circuits Concealed in Ceilings, Walls, and Partitions: Mineral-insulated, metal-sheathed cable, Type MI.

Coordinate "Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground" Paragraph below with Section 260543 "Underground Ducts and Raceways for Electrical Systems."

        - Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground: Mineral-insulated, metal-sheathed cable, Type MI.

        - Branch Circuits Installed below Raised Flooring: Mineral-insulated, metal-sheathed cable, Type MI.

        - Branch Circuits in Cable Tray: Mineral-insulated, metal-sheathed cable, Type MI.

      - INSTALLATION, GENERAL

        - Complete raceway installation between conductor and cable termination points in accordance with Section 260533 "Raceway and Boxes for Electrical Systems" prior to pulling conductors and cables.

        - Use pulling means, including cable, rope, and basket-weave wire/cable grips, that will not damage cables or raceway.

        - Install exposed cables parallel and perpendicular to surfaces of exposed structural members, and follow surface contours where possible.

        - Support cables in accordance with Section 260529 "Hangers and Supports for Electrical Systems."

        - Complete cable tray systems installation in accordance with Section 260536 "Cable Trays for Electrical Systems" prior to installing conductors and cables.

      - INSTALLATION OF MINERAL INSULATED (MI) CABLE

Refer to nVent PYROTENAX Installation Manual H57864. See Pyrotenax.nvent.com for installation videos.

        - Examination:

          - Examine surfaces and substrates to receive wiring cables for compliance with requirements for installation tolerances and other conditions affecting performance.

            - Prior to installation of wiring cable system, verify that all mounting structures are suitably fire rated.

            - Ensure surfaces in contact with wiring cables are free of burrs and sharp protrusions.

            - Ensure mounting structures are suitably spaced per installation manual.

            - Ensure system for pulling of cable into final locations is suitable per guidelines in installation manual.

        - Preinstallation Testing:

          - Prior to pulling wiring cable into place, an insulation resistance test shall be performed by installing contractor to ensure integrity of wiring cable as described in the installation manual.

          - Proceed with installation only after any unsatisfactory conditions have been corrected.

        - Preparation:

          - Protect all wiring cable ends from moisture ingress until cable is terminated with end seals.

        - Installation:

          - In the field, all wiring cables shall be meggered with 500 V dc for MI 300 V and 600 V cables. The following field megger readings shall be taken on each cable:

            - Wiring cable shall be meggered when received at Project site before installation.

            - Wiring cable shall be meggered after sealing termination of the MI cable, prior to being attached to the gear, breaker, etc.

            - Insulation resistance must exceed 200 megohms at 500 V dc.

            - All results must meet manufacturer's specification.

      - INSTALLATION OF FIRE-ALARM WIRE AND CABLE

        - Comply with NFPA 72.

Refer to nVent PYROTENAX Installation Manual H57864. See www.nvent.com/PYROTENAX for installation videos.

        - Examination:

          - Examine surfaces and substrates to receive wiring cables for compliance with requirements for installation tolerances and other conditions affecting performance.

            - Prior to installation of wiring cable system, verify that all mounting structures are suitably fire rated.

            - Ensure surfaces in contact with wiring cables are free of burrs and sharp protrusions.

            - Ensure mounting structures are suitably spaced per installation manual.

            - Ensure system for pulling of cable into final locations is suitable per guidelines in installation manual.

        - Preinstallation Testing:

          - Prior to pulling wiring cable into place, an insulation resistance test shall be performed by installing contractor to ensure integrity of wiring cable as described in the installation manual.

          - Proceed with installation only after any unsatisfactory conditions have been corrected.

        - Preparation:

          - Protect all wiring cable ends from moisture ingress until cable is terminated with end seals.

        - Installation:

          - In the field, all wiring cables shall be meggered with 500 V dc for MI 300 V and 600 V cables. The following field megger readings shall be taken on each cable:

            - Wiring cable shall be meggered when received at Project site before installation.

            - Wiring cable shall be meggered after sealing termination of the MI cable, prior to being attached to the gear, breaker, etc.

            - Insulation resistance must exceed 200 megohms at 500 V dc.

            - All results must meet manufacturer's specification.

        - Wiring Method: Install wiring in metal pathway in accordance with Section 270529 "Hangers and Supports for Communications Systems."

          - Install plenum cable in environmental airspaces, including plenum ceilings.

          - Fire-alarm circuits and equipment control wiring associated with fire-alarm system must be installed in a dedicated pathway system.

            - Cables and pathways used for fire-alarm circuits, and equipment control wiring associated with fire-alarm system, may not contain any other wire or cable.

          - Fire-Rated Cables: Use of two-hour, fire-rated fire-alarm cables, NFPA 70, Type MI, is permitted.

          - Signaling Line Circuits: Power-limited fire-alarm cables may be installed in the same cable or pathway as signaling line circuits.

        - Wiring within Enclosures: Separate power-limited and non-power-limited conductors as recommended by manufacturer. Install conductors parallel with or at right angles to sides and back of the enclosure. Bundle, lace, and train conductors to terminal points with no excess. Connect conductors that are terminated, spliced, or interrupted in any enclosure associated with fire-alarm system to terminal blocks. Mark each terminal in accordance with system's wiring diagrams. Make all connections with approved crimp-on terminal spade lugs, pressure-type terminal blocks, or plug connectors.

        - Cable Taps: Use numbered terminal strips in junction, pull, and outlet boxes; cabinets; or equipment enclosures where circuit connections are made.

        - Color-Coding: Color-code fire-alarm conductors differently from the normal building power wiring. Use one color-code for alarm circuit wiring and another for supervisory circuits. Color-code audible alarm-indicating circuits differently from alarm-initiating circuits. Use different colors for visible alarm-indicating devices. Paint fire-alarm system junction boxes and covers red.

      - CONNECTIONS

        - Tighten electrical connectors and terminals in accordance with manufacturer's published torque-tightening values.

Use nVent PYROTENAX connectors and splices options as described in Part 2 of this Section.

        - Use manufacturer’s terminations and/or field splices.

        - Comply with requirements in [Section 284621.11 "Addressable Fire-Alarm Systems"] [Section 284621.13 "Conventional Fire-Alarm Systems"] for connecting, terminating, and identifying wires and cables.

      - IDENTIFICATION

        - Identify and color-code conductors and cables in accordance with Section 260553 "Identification for Electrical Systems."

        - Identify each spare conductor at each end with identity number and location of other end of conductor, and identify as spare conductor.

      - SLEEVE AND SLEEVE-SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

        - When required, install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 260544 "Sleeves and Sleeve Seals for Electrical Raceways and Cabling."

      - FIRESTOPPING

        - Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly in accordance with Section 078413 "Penetration Firestopping."

      - FIELD QUALITY CONTROL

Coordinate "Tests and Inspections" Paragraph below with "Qualifications" and "Field Quality Control" articles in Section 260010 "Supplemental Requirements for Electrical."

        - Tests and Inspections:

          - After installing conductors and cables and before electrical circuitry has been energized, test all conductors for compliance with requirements.

          - Perform each of the following visual and electrical tests:

            - Inspect exposed sections of conductor and cable for physical damage and correct connection in accordance with the single-line diagram.

            - Test bolted connections for high resistance using one of the following:

              - Low-resistance ohmmeter.

              - Calibrated torque wrench.

            - Inspect for correct identification.

            - Inspect cable jacket and condition.

            - Insulation-resistance test on each conductor for ground and adjacent conductors. Apply a potential of 500 V( dc) for 300 V and 600 V cable for a one-minute duration.

            - Continuity test on each conductor and cable.

            - Uniform resistance of parallel conductors.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Installation will be considered failed if it does not pass tests and inspections.

        - Prepare test and inspection reports to record the following:

          - Procedures used.

          - Results that comply with requirements.

          - Results that do not comply with requirements, and corrective action taken to achieve compliance with requirements.

END OF SECTION 260519